## Proracun
Bor-plastika d.o.o. |  |  |  | 2 Glavna Str. |  | Tel.: +385/31/732-187
31309 Kn. Vinogradi
Email: proizvodnja@bor-plastika.hr
Selection of nominal size of separator for light liquids
Calculation of storm water |  | Qr = φ * i * A |  |  |  | Σ Qr = | Qri | Ai
Outflow coefficient φ : |  | 0.9 |  |  |  |  | 14.58 | 1000
Storm water intensity i: |  | 162 | l.s-1.ha-1 |  |  | Σ Qr = | 14.58 | 1000
Area A: |  | 1000 | m2
Calculation of wastewater |  | Qs = Qs1 + Qs2 + Qs3
- Drain valve Qs1 |  |  | Anzahl
| Valve DN 25, R1 : |  | 0
| Valve DN 20, R3/4 : |  | 0
| Valve DN 15, R1/2 : |  | 0 | => Qs1 = | 0 | l/s
- Carwash Qs2 |  |  | 0 | => Qs2 = | 0 | l/s
- High-pressure washing devices Qs3 |  |  | 0 | => Qs3 = | 0 | l/s
|  |  |  | Σ Qs = | 0 | l/s
Selection of nominal size of separating device |  |  | NS = (Qr + fx*Qs) * fd
Coefficient fx : |  | 2
Specific weight coefficient LK fd : |  | 1
Storm water Qr [l.s-1]: |  | 14.58 | <=
Wastewater Qs [l.s-1]: |  | 0 | <=
Nominal size: 14,6
Selection of sedimentation tank of light liquids separator
Amount of sludge: |  | Insignificant: | - wastewater treatment with slightly defined amount of sludge
- all surfaces that absorb rainfall, with only minor amounts of impurities from the traffic from the streets or the like
|  | Medium: | - gas stations, manual car washes, spare parts washes, stands for washing buses
- wastewater from the repair shop, the surfaces on which vehicles are left, power plants
|  | Large: | - vehicles wash on construction sites, agricultural machines, washing columns
- automatic car washes, for example portal laundries, streets for washing
With absorption filter:
Suggested type: BP OLEX 15 L/KF
New calculation is started by pressing the button "new calculation".
15 min. rainfall intensity with periodicity of 0,5 or 1,0.
Periodicity: 0,5 - Settlements with more than 5000 inhabitants
- city centers, industrial areas, smaller plants
1,0 - Settlements with more than 5000 inhabitatns
- rural areas, industrial areas with separate grid

## Uputstvo
Uputstvo programa
Program se sastoji od tri dijela, koje ćete pronaći u listu "proračun".
Prvi dio namjenen je za proračun oborinske vode.
Postupak: Birajte koeficient odljeva iz registra desno od žutog polja, te će se vrijednost sama pojaviti u žutom polju. Jednaki postupak je i pri intenzitetu oborina, pri kojem takoder možemo birati periodičnost vode. Površina se pripisuje samo ručno. Nakon ispisivanja triju vrijednosti pristisnite rubriku (tipku) "Dodati Qr", nakon čega ce se pojaviti vrijednost u desnoj tabeli, gdje je iznos Qr označen zeleno. Tada možemo promijeniti vrijednosti u žutim ćelijama, te nanovo pritisnuti na tipku "Dodati Qr". Rezultat ce biti zaračunat.
Drugi dio se odnosi na proračun otpadne vode. Dovoljno je navesti količinu u žute ćelije te potom pritisnti tipku "Izračunaj Qs" i Qs ce biti izračunat u zelenoj ćeliji.
Treći dio namijenjem je određivanju veličine taložnice separatora lakih tekućina. Koeficient fx je fiksno odreden. Birajte samo koeficijent specijalne težine iz registra ili ručno upišite. Ukoliko želite upotrijebiti vrijednosti iz prethodnih dijelova, tada pritisnite na gumb "Preuzeti iz proračuna", i vrijednosti će se same pokazati. Ove vrijednosti takoder možete dobiti bez prethodnog dijela programa. U tom slučaju ćete pritisnuti na gumb "Izračunati NS". Zatim birajte količinu mulja i opremu sa absorpcijskim filterom. Na kraji pritisnie gumb "plan tipa", i proračun je gotov.
Za novi proračun pritisnite "Novi proračun".
Nakon uvoda programa pritisnite "makrodopuštenje" u protivnom proračunavanje neće funkcionirati.
Puno uspjeha
Bor-plastika d.o.o.

## Data (hidden)
1 |  | 4 |  | 1 | 14.58 | 1000 | 1
koeficient odljeva | 0 | intenzitet oborinske vode | 0 | 0 | 2 |  | do 0,85 g/cm3 | 1 | DN15, R1/2 | 0.5 | 0.5 | 0.35 | 0.25 | 0.1
krovovi (1,0) | 1 | Dubrovnik | 475 | 161 | periodičnost | 0 | preko 0,85 do 0,90 g/cm3 | 1.5 | DN20, R3/4 | 1 | 1 | 0.7 | 0.5 | 0.2
asfaltne i betonske površine (0,9) | 0.9 | Karlovac | 410 | 144 | 0.5 | 0.5 | preko 0,90 do 0,95 g/cm3 | 2 | DN25, R1 | 1.7 | 1.7 | 1.2 | 0.85 | 0.3
normalni plaster (0,7) | 0.7 | Osijek | 245 | 162 | 1 | 1
šljunčane površine (0,5) | 0.5 | Pula | 310 | 143 |  |  | 2 |  | 2
propusne površine (0,3) | 0.3 | Rijeka | 555 | 158 |  |  | mala | 200 | da | 1
|  | Split | 315 | 139 |  |  | srednja | 200 | ne | 0
|  | Zadar | 375 | 128 |  |  | velika | 300
|  | Zagreb | 315 | 162
|  |  |  | 144 |  |  | 1.5 | 3 | 3 | 14.6
|  |  |  | 157 |  |  | 3 | 6 | 6 | 1
|  |  |  | 150 |  |  | 6 | 10 | 10
|  |  |  | 164 |  |  | 10 | 15 | 15
|  |  |  | 143 |  |  | 15 | 20 | 20
|  |  |  | 170 |  |  | 20 | 30 | 30
|  |  |  | 166 |  |  | 30 | 50 | 50
|  |  |  | 158 |  |  | 30 | 65 | 65
|  |  |  | 170 |  |  | 30 | 80 | 80
|  |  |  | 151 |  |  | 30 | 100 | 100
|  |  |  | 170 |  |  | 30 | 125 | 125
175